## Parameter-HMI-01CONV-01-MCU-01-
MODBUS RTU / RS-485 INTERFACE
Parameter | HMI-01 / CONV-01 | MCU-01 | Design value
Network role | Modbus RTU Master | Modbus RTU Slave | HMI initiates polling
Physical layer | USB to RS-485 converter | RS-485 2-wire | Half-duplex differential link
Slave address | Master | 1 | MCU-01 Modbus slave ID
Baud rate | 9600 bps | 9600 bps | Must match both ends
Frame format | 8 data / no parity / 1 stop | 8N1 | Must match both ends
Poll interval | 250 ms nominal | Response required | Per 018 Sheet 2
Response timeout | 1000 ms | - | Fault threshold
Retry count | 3 attempts | - | Before HMI alarm event
Termination | 120 Ohm at end of bus | 120 Ohm at end of bus | 120 Ohm Across data pair At two physical end points only
Cable | Shielded twisted pair | Shielded twisted pair | Data pair + Cable shield