## No-Pre-condition-Verificationme
PRE-COMMISSIONING READINESS MATRIX
No. | Pre-condition | Verification method | Expected result | Actual result | Result | Reference
1 | Latest approved PLC, HMI, and communication drawings available | Verify drawing revision | DWG 011~019 approved revision available |  |  | DWG 011~018
2 | PLC-01 power and CPU status normal | Inspect PLC power / diagnostic LED | PLC powered, CPU normal, no hardware fault |  |  | DWG 011
3 | HMI-01 LabVIEW SCADA application installed | Launch HMI application | HMI starts without application error |  |  | DWG 016 / 017
4 | PLC-01 Ethernet physical link complete | Inspect RJ45 / link LED | Ethernet link active at HMI-01 and PLC-01 |  |  | DWG 018 SHT 1
5 | CONV-01 installed and powered | Inspect converter / USB interface | USB/Serial converter recognized by HMI-01 |  |  | DWG 018 SHT 1
6 | MCU-01 RS-485 wiring complete | Verify D0/D1 or A/B terminal marking | Data pair polarity matches actual device terminal markings |  |  | DWG 018 SHT 1
7 | RS-485 termination / shield arrangement verified | Inspect installed wiring | 120 Ohm at two physical endpoints only; shield arrangement per approved note |  |  | DWG 018 SHT 1
8 | PLC/HMI static IP configuration complete | Verify configured IPv4 settings | HMI-01 = 192.168.10.10; PLC-01 = 192.168.10.20; Mask = 255.255.255.0 |  |  | DWG 018 SHT 1
9 | MCU serial settings configured | Verify converter and MCU settings | 9600 bps / 8N1 / MCU Slave ID 1 |  |  | DWG 018 SHT 1
10 | Safety circuit and machine area ready for test | Verify E-Stop reset, guarding, authorized test area | Safety conditions approved before functional command test |  |  | DWG 011 / 013